MODBUS Address-table UCM 5 - V1.0

Function code 3

| Address |  |  |  |
| --- | --- | --- | --- |
| DEC | HEX | L/H | Register name | Info / Range of values |
| 0 | 00 | 00 |  | Reactive Power | Signed 32-bit, Unit: var Input 1, Impulse time * impulse ratio |
| 1 | 00 | 01 |  |  |  |
| 2 | 00 | 02 |  | Active Power | Signed 32-bit, Unit: W Input 2, Impulse time * impulse ratio |
| 3 | 00 | 03 |  |  |  |
| 4 | 00 | 04 |  | Apparent Power | Signed 32-bit, Unit: VA |
| 5 | 00 | 05 |  |  |  |
| 9 | 00 | 09 | L | IO-State | Byte, Bit 1..5 High: Input/Output is active, Low: Input/Output is not active |
| 10 | 00 | 0A |  | IN 1 | Pulses of actual synch-period | Signed 32-bit Impulse counter of actual synch-period. After synch event the impulses of the hole synch-period are stored in pulses of previous synch-period and the pulse counter is set to zero |
| 11 | 00 | 0B |  |  |  |  |
| 12 | 00 | 0C |  | IN 2 |  |  |
| 13 | 00 | 0D |  |  |  |  |
| 14 | 00 | 0E |  | IN 3 |  |  |
| 15 | 00 | 0F |  |  |  |  |
| 16 | 00 | 10 |  | IN 4 |  |  |
| 17 | 00 | 11 |  |  |  |  |
| 18 | 00 | 12 |  | IN 5 |  |  |
| 19 | 00 | 13 |  |  |  |  |
| 20 | 00 | 14 |  | IN 1 | Pulses of previous-synch period (complete synch period) | Signed 32-bit Impulses of last synch period |
| 21 | 00 | 15 |  |  |  |  |
| 22 | 00 | 16 |  | IN 2 |  |  |
| 23 | 00 | 17 |  |  |  |  |
| 24 | 00 | 18 |  | IN 3 |  |  |
| 25 | 00 | 19 |  |  |  |  |
| 26 | 00 | 1A |  | IN 4 |  |  |
| 27 | 00 | 1B |  |  |  |  |
| 28 | 00 | 1C |  | IN 5 |  |  |
| 29 | 00 | 1D |  |  |  |  |
| 30 | 00 | 1E |  | IN 1 | Time since the last impulse | Signed 32-bit, Unit ms Time since the last impulse. If a new impulse occurs the value of this timer is stored in Timer of previous impulse and the timer is set to zero. In case of synch-input it is the time since the last synch-event. |
| 31 | 00 | 1F |  |  |  |  |
| 32 | 00 | 20 |  | IN 2 |  |  |
| 33 | 00 | 21 |  |  |  |  |
| 34 | 00 | 22 |  | IN 3 |  |  |
| 35 | 00 | 23 |  |  |  |  |
| 36 | 00 | 24 |  | IN 4 |  |  |
| 37 | 00 | 25 |  |  |  |  |
| 38 | 00 | 26 |  | IN 5 |  |  |
| 39 | 00 | 27 |  |  |  |  |
| 40 | 00 | 28 |  | IN 1 | Time of previous impulse | Signed 32-bit, Unit ms Time of previous impulse. In case of synch-input it is the time of the previous synch-period. |
| 41 | 00 | 29 |  |  |  |  |
| 42 | 00 | 2A |  | IN 2 |  |  |
| 43 | 00 | 2B |  |  |  |  |
| 44 | 00 | 2C |  | IN 3 |  |  |
| 45 | 00 | 2D |  |  |  |  |
| 46 | 00 | 2E |  | IN 4 |  |  |
| 47 | 00 | 2F |  |  |  |  |
| 48 | 00 | 30 |  | IN 5 |  |  |
| 49 | 00 | 31 |  |  |  |  |
| 50 | 00 | 32 |  | IN 1 | Sum of all pulses | Signed 32-bit Sum of all impulses. Note: It is not possible to count impulses if the device is not powered. |
| 51 | 00 | 33 |  |  |  |  |
| 52 | 00 | 34 |  | IN 2 |  |  |
| 53 | 00 | 35 |  |  |  |  |
| 54 | 00 | 36 |  | IN 3 |  |  |
| 55 | 00 | 37 |  |  |  |  |
| 56 | 00 | 38 |  | IN 4 |  |  |
| 57 | 00 | 39 |  |  |  |  |
| 58 | 00 | 3A |  | IN 5 |  |  |
| 59 | 00 | 3B |  |  |  |  |
| 60 | 00 | 3C |  | IN 1 | Power | Signed 32-bit, Unit: W, VA, var Input-impulse-time * Input-impulse-ratio |
| 61 | 00 | 3D |  |  |  |  |
| 62 | 00 | 3E |  | IN 2 |  |  |
| 63 | 00 | 3F |  |  |  |  |
| 64 | 00 | 40 |  | IN 3 |  |  |
| 65 | 00 | 41 |  |  |  |  |
| 66 | 00 | 42 |  | IN 4 |  |  |
| 67 | 00 | 43 |  |  |  |  |
| 68 | 00 | 44 |  | IN 5 |  |  |
| 69 | 00 | 45 |  |  |  |  |
| 70 | 00 | 46 |  | IN 1 | Maximum pulses of synch-period associated by synch-time | Signed 32-bit Maximum pulses are stored if synch-event occurs within synch-time ( + 10% ) |
| 71 | 00 | 47 |  |  |  |  |
| 72 | 00 | 48 |  | IN 2 |  |  |
| 73 | 00 | 49 |  |  |  |  |
| 74 | 00 | 4A |  | IN 3 |  |  |
| 75 | 00 | 4B |  |  |  |  |
| 76 | 00 | 4C |  | IN 4 |  |  |
| 77 | 00 | 4D |  |  |  |  |
| 78 | 00 | 4E |  | IN 5 |  |  |
| 79 | 00 | 4F |  |  |  |  |
| 80 | 00 | 50 |  | IN 1 | Maximum pulses of synch-period | Signed 32-bit Maximum pulses between tow synch-events |
| 81 | 00 | 51 |  |  |  |  |
| 82 | 00 | 52 |  | IN 2 |  |  |
| 83 | 00 | 53 |  |  |  |  |
| 84 | 00 | 54 |  | IN 3 |  |  |
| 85 | 00 | 55 |  |  |  |  |
| 86 | 00 | 56 |  | IN 4 |  |  |
| 87 | 00 | 57 |  |  |  |  |
| 88 | 00 | 58 |  | IN 5 |  |  |
| 89 | 00 | 59 |  |  |  |  |
| 90 | 00 | 5A |  | IN 1 | Time of synch-period of maximum pulses | Unsigned 16-bit, Unit sec Time of synch-period of maximum pulses event |
| 91 | 00 | 5B |  | IN 2 |  |  |
| 92 | 00 | 5C |  | IN 3 |  |  |
| 93 | 00 | 5D |  | IN 4 |  |  |
| 94 | 00 | 5E |  | IN 5 |  |  |
| 96 | 00 | 60 |  | Internal use | 10 |
| 101 | 00 | 65 |  | SETTINGS | See settings section for further details |
| … |  |  |  |  |  |
| 255 | 00 | FF | H | Hardware identify. | 10 |
|  |  |  | L | Software-version | Byte – exp.: 10 ( V1.0 |
| 998 | 03 | E6 | W | EEPROM-state | Internal use |
| 999 | 03 | E7 | W | Memory-counter | Number of data-lines in the data-memory |
| 1000 | 03 | E8 | W | IN 1 | Pulses of last periods | Signed 16-bit, Range: 0..32768, Error = -1 IN 1 exp.: 1000 = last period, 1001 = 1 period before, 1002 2 periods before, 1003 … |
| … |  |  |  |  |  |  |
| 2000 | 07 | D0 | W | IN 2 |  |  |
| … |  |  |  |  |  |  |
| 3000 | 0B | B8 | W | IN 3 |  |  |
| … |  |  |  |  |  |  |
| 4000 | 0F | A0 | W | IN 4 |  |  |
| … |  |  |  |  |  |  |
| 5000 | 13 | 88 | W | IN 5 |  | Signed 16-bit, Unit sec, Range: 0..32768, Error = -1 Duration of synch-period |
| … |  |  |  |  |  |  |

Controller settings (read / write)

| Address |  |  |  |
| --- | --- | --- | --- |
| Code R= 3 | Code W= 6 | H/L | Register name | Reset value | Description / Range of values / Examples |
| 101 | 101 | H | Baud rate (Password: H=L) | 0 | Byte 0 = 9600, 1= 19200, 2 = 38400, other values= 38400 |
|  |  | L | Baud rate | 2 |  |
| 102 | 102 | L | Reserved (Mode) | 0 | Byte, not used |
| 103, 104 | 103, 104 |  | IN 1 | Impulse-ratio | 1 | Single, Unit: Impulse / kWh Input-impulse-ratio is used to calculate the actual power |
| 105, 106 | 105, 106 |  | IN 2 |  |  |  |
| 107, 108 | 107, 108 |  | IN 3 |  |  |  |
| 109, 110 | 109, 110 |  | IN 4 |  |  |  |
| 111, 112 | 111, 112 |  | IN 5 |  |  |  |
| 113 | 113 | L | Input-Debounce-Time | 5 | Byte, Unit ms - Impulse-length that are shorter than the debounce-time will be ignored. |
| 114 | 114 | L | Number of pulse-times | 2 | Byte, Valid range: 0..4 – Number of last pulse-times to calculate power (if values > 4 will set 4) |
| 115 | 115 | L | Synch-Mode | 0 | 0= Synch with impulse at synch-input 1= Synch with internal timer (synch-time) |
| 116 | 116 | W | Synch-Time | 0 | Unsigned 16-bit, Unit sec Synch-mode= 0: store max. pulses associated by this time Synch-mode= 1: Simulate synch-impulse after this time |
| - | 120 | L | Clear pulse sum counter | - | Bit 1..5 for IN 1..5. If bit is set clear sum pulse counter exp.: 0h06 ( clear counter for IN 1 and IN 2 |
| - | 121 | L | Clear pulse counter of actual period | - | Bit 1..5 for IN 1..5. If bit is set clear pulse counter exp.: 0h06 ( clear counter for IN 1 and IN 2 |
| - | 122 | L | Clear max. pulses per period register | - | Clear all max pulses registers |
| - | 123 | L | Clear pulse register of last periods | - | Write 0h3E to clear |

History

V1.0

- Initial Version

V1.1

- Impulse-ratio as single (add 5 word)